## Instructions
Instructions for use:
NOTE: This spreadsheet is intended to determine the constant condenser temperature unloading curve for input into System Analyzer(TM) or TRACE(TM).
In order for this to work correctly you need to be sure that the unloading curve you have includes ambient (condenser) relief.
- Select the appropriate sheet (10% Loads or NPLV) for the unloading curve that you have by clicking on the appropriate button.
- Input the amount of ambient relief for the type of chiller in question. Approximate values are given as notes by placing your cursor over the ambient relief field.
- Enter the kW consumed at the varying load percentages.
Note: The load percentages can be changed but all subsequent inputs must be changed to reflect it.
Note: Only input data that you have. If you don't have data, input 0 for the kW and ignore that output.
- Enter the appropriate condenser entering temperatures for which the kW were calculated at the specific load percentage.
- The spreadsheet will calculate the new kW percentages for input into System Analyzer or TRACE.
- If you have any questions please contact the C.D.S.(TM) Support Center.
- User input field
- Inputs for System Analyzer or TRACE
- Calculation fields (not to be used)

## 10% Loads
10% Load Increment Calculation Sheet
Ambient relief/degree of relief | 1.6%
S.A. and TRACE Inputs | [7 empty] | S.A. and TRACE Inputs
Load %* | kW | ECWT | kW% (selection) | DeltaT | % Relief | Ambient multiplier | kW @ Constant ECWT | % kW @ Constant ECWT
100% | 100 | 85 | 100% | 0 | 0 | 1 | 100 | 100%
90% | 90 | 81 | 90% | 4 | 0.064 | 0.936 | 96.1538 | 96.15%
80% | 80 | 77 | 80% | 8 | 0.128 | 0.872 | 91.7431 | 91.74%
70% | 70 | 73 | 70% | 12 | 0.192 | 0.808 | 86.6337 | 86.63%
60% | 60 | 69 | 60% | 16 | 0.256 | 0.744 | 80.6452 | 80.65%
50% | 50 | 65 | 50% | 20 | 0.32 | 0.68 | 73.5294 | 73.53%
40% | 40 | 65 | 40% | 20 | 0.32 | 0.68 | 58.8235 | 58.82%
30% | 30 | 65 | 30% | 20 | 0.32 | 0.68 | 44.1176 | 44.12%
20% | 20 | 65 | 20% | 20 | 0.32 | 0.68 | 29.4118 | 29.41%
10% | 10 | 65 | 10% | 20 | 0.32 | 0.68 | 14.7059 | 14.71%
* These percentages can be changed
- User input field
- Inputs for System Analyzer or TRACE
- Calculation fields (not to be used)
Note on B3: Approximate Ambient Relief numbers Two stage Centrifugal = 1.5% Two stage Centrifugal with VFD = 2.3% Screw Chiller = 1.6% Single stage centrifugal = 0.9% Single stage centrifugal with VFD = 2.3% OR, input the "Condenser Relief" number from the piece of equipment you are using in System Analyzer(TM) or TRACE(TM)

## NPLV
NPLV Calculation Sheet
Ambient relief/degree of relief | 1.6%
S.A. and TRACE Inputs | [7 empty] | S.A. and TRACE Inputs
Load %* | kW | ECWT | kW% (selection) | DeltaT | % Relief | Ambient multiplier | kW @ Constant ECWT | % kW @ Constant ECWT
100% | 100 | 85 | 100% | 0 | 0 | 1 | 100 | 100%
75% | 75 | 75 | 75% | 10 | 0.16 | 0.84 | 89.2857 | 89.29%
50% | 50 | 65 | 50% | 20 | 0.32 | 0.68 | 73.5294 | 73.53%
25% | 25 | 65 | 25% | 20 | 0.32 | 0.68 | 36.7647 | 36.76%
*These percentages can be changed
- User input field
- Inputs for System Analyzer or TRACE
- Calculation fields (not to be used)
Note on B3: Approximate Ambient Relief numbers Two stage Centrifugal = 1.5% Two stage Centrifugal with VFD = 2.3% Screw Chiller = 1.6% Single stage centrifugal = 0.9% Single stage centrifugal with VFD = 2.3% OR, input the "Condenser Relief" number from the piece of equipment you are using in System Analyzer(TM)