## Instructions
Equation Calculator for USGBC LEED: v4 Energy & Atmosphere Credit; BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8
Purpose
This calculation tool automatically solves the equations described in the USGBC document, LEED for New Construction Version 2.2. Use it to quickly determine whether the HVAC equipment-and-refrigerant combinations in a prospective LEED-NC project comply with the requirements of Energy & Atmosphere Credit 4.
How to use the calculator
NOTE: You may only enter values in turquoise-colored cells. All other entries either are calculated automatically or are fixed values.
1. Choose a worksheet by clicking the appropriate tab at the bottom of the Excel window. Pick the Single Unit worksheet to provide information for a single piece of equipment. Or, pick the Multiple Units worksheet to describe a project with different types of equipment and/or refrigerant.
2. Type the job name in cell B2.
3. Type the location of the job in cell B3.
4. OPTIONAL: Enter the appropriate unit tag(s) from the equipment schedule in cell(s) B5 through G5.
5. Enter the refrigerant type in cell(s) B6 through G6. Selecting the refrigerant type automatically inserts the appropriate GWP and ODP values from the LEED-NC v4 Reference Guide (EA Credit 4, Table 1) in rows 14 and 15, respectively.
6. Enter the equipment type in cell(s) B7 through G7. Selecting the equipment type automatically inserts the appropriate equipment life value(s) from the LEED-NC v4 Reference Guide in row 12.
7. For each refrigerant type and equipment type, enter the HVAC mechanical cooling capacity in cell(s) B8 through G8. If multiple units use the same refrigerant type, enter the sum of their capacities.
8. For each refrigerant type/equipment type combination, enter the HVAC refrigerant charge, in pounds, in cell(s) B9 through G9. If multiple units of the same equipment type use the same refrigerant type, enter the sum of their refrigerant charges in pounds.
8A. (For Multiple Unit worksheet only) Enter the number of identical units in Row 10.
The project qualifies for EA Credit 4 of LEED-NC v4 if the value in cell H21 (Multiple Unit worksheet) or C21 (Single Unit worksheet) is less than or equal to 100 and “Yes” is displayed in cell H22 or C22.
The project does not quality for this credit if the value in cell H22 (Multiple Unit worksheet) or C21 (Single Unit worksheet) is greater than 100 and “No” is displayed in cell C22 or H23.
9. OPTIONAL: To provide additional information about the project, type your comments in cell A87 (Multiple Unit A88)
10. To print the caluclation results for your records and/or as documentation for your LEED project submittal, either click the Print button in the toolbar or open the File menu and select Print.
The report is automatically stamped with the date and time of the last calculation (cell B46).

## Single Unit
Equation Calculator for USGBC LEED: v4 Energy & Atmosphere Credit; BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8
Job name
Job location
Date and time of calculation | 2014-04-28 09:55
Unit tag(s) |  | All
Refrigerant type | R-123 | Qtotal
Equipment type | Centrifugal chiller
Capacity, tons (Qunit) | 1 | 1
Refrigerant charge, lb | 2
Refrigerant charge, lb/ton (Rc) | 2
Leak rate, % of charge per year (Lr) | 2%
Equipment life (Life) | 25
End-of-life refrigerant loss, % of charge (Mr) | 10%
Global warming potential of refrigerant (GWPr) | 77
Ozone depletion potential of refrigerant (ODPr) | 0.02
Life-cycle direct global warming potential (LCGWP) | 3.696
Life-cycle ozone depletion potential (LCODP) | 0.00096
TSAC factor | 99.696
TSAC factor × capacity | 99.696 | 99.696
| Calculation | 99.696
| Credit? | Yes
Version 4 “Equation Calculator” for LEED, BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8;
© 2013 Trane. All rights reserved
Trane, in providing this calculation tool, assumes no responsibility for the performance or desirability of any resulting system design. Design of the HVAC system is the prerogative and responsibility of the engineering professional.
LEED Energy and Atmosphere Credit Submittal
Version 4 “Equation Calculator” for LEED, BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8;
Job name
Job location
Date | 2014-04-28 09:55
If only one type of refrigerant is used, the HVAC&R systems | comply with the formula:
OR
If multiple refrigerant types are used, the HVAC&R systems | comply with the formula:
RESULT
Using the appropriate equation, the final calculation equals | 99.696
Based on the LEED v4 for Enhanced Refrigerant Management this project | qualifies.
CALCULATIONS
Defaults used:
2% Leakage rate per year (Lr) (except as explicitly doucmented & allowed by USGBC)
10% End-of-life loss of charge (Mr)
Equipment life varies by equipment type
ODP and GWP from LEED v4 BD+C Reference Guide
Entered values:
R-123
Unit tag(s)
Capacity, tons (Qunit) | 1
Refrigerant charge, lb | 2
Refrigerant charge, lb/ton (Rc) | 2
Global warming potential of refrigerant (GWPr) | 77
Ozone depletion potential of refrigerant (ODPr) | 0.02
LCGWP + 100,000 × LCODP | 99.696
Total capacity, tons | 1
Result: | 99.696
REMARKS
Note on A8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on B8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on A9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on B9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on A11: In 2006 leak rate data for Trane R-123 centrifugal chillers was submitted to the USGBC. A 0.5% annual leakage rate is approved for these chillers per a CIR published at www.usgbc.org
Orange = Fixed values
Turquoise = User entries
Yellow = Calculated values
Red = Ineligible result
Green = Eligible result
Red = Ineligible result

## Multiple Units
Equation Calculator for USGBC LEED: v4 Energy & Atmosphere Credit; BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8
Job name
Job location
Date and time of calculation | 2014-04-28 09:55
Unit tag(s) | [6 empty] | All
Refrigerant type | R-123 | R-123 | R-22 | Water | R-407c | R-410a | Qtotal | 0
Equipment type | Centrifugal chiller | Centrifugal chiller | Screw chiller | Absorption chiller | Scroll chiller | Packaged AC or HP
Capacity, tons (Qunit) | 1000 | 0 | 0 | 0 | 0 | 0 | 1000
Refrigerant charge, lb | 400 | 0 | 0 | 0 | 0 | 0
Quantity of identical units | 1 | 1 | 1 | 1 | 1 | 1
Refrigerant charge, lb/ton (Rc) | 0.4 | 0 | 0 | 0 | 0 | 0
Leak rate, % of charge per year (Lr) | 2% | 2% | 2% | 2% | 2% | 2%
Equipment life (Life) | 25 | 25 | 25 | 23 | 20 | 15
End-of-life refrigerant loss, % of charge (Mr) | 10% | 10% | 10% | 10% | 10% | 10%
Global warming potential of refrigerant (GWPr) | 77 | 77 | 1810 | 4000 | 1770 | 2080
Ozone depletion potential of refrigerant (ODPr) | 0.02 | 0.02 | 0.04 | 0 | 0 | 0
Life-cycle direct global warming potential (LCGWP) | 0.7392 | 0 | 0 | 0 | 0 | 0
Life-cycle ozone depletion potential (LCODP) | 0.000192 | 0 | 0 | 0 | 0 | 0
TSAC factor | 19.9392 | 0 | 0 | 0 | 0 | 0
TSAC factor × capacity | 19939.2 | 0 | 0 | 0 | 0 | 0 | 19939.2
| Weighted calculation | [5 empty] | 19.9392
| Credit? | [5 empty] | Yes
Version 4 “Equation Calculator” for LEED, BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8;
© 2013 Trane. All rights reserved
Trane, in providing this calculation tool, assumes no responsibility for the performance or desirability of any resulting system design. Design of the HVAC system is the prerogative and responsibility of the engineering professional.
LEED Energy and Atmosphere Credit Submittal
Version 4 “Equation Calculator” for LEED, BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8;
Job name
Job location
Date | 2014-04-28 09:55
If only one type of refrigerant is used, the HVAC&R systems | comply with the formula:
OR
If multiple refrigerant types are used, the HVAC&R systems | comply with the formula:
RESULT
Using the appropriate equation, the final calculation equals | 19.9392
Based on the LEED v4 for Enhanced Refrigerant Management this project | qualifies.
CALCULATIONS
Defaults used:
2% Leakage rate per year (Lr) (except as explicitly doucmented & allowed by USGBC)
10% End-of-life loss of charge (Mr)
Equipment life varies by equipment type
ODP and GWP from LEED v4 BD+C Reference Guide
Entered values:
| R-123 | R-123 | R-22 | Water | R-407c | R-410a
Unit tag(s)
Capacity, tons (Qunit) | 1000 | 0 | 0 | 0 | 0 | 0
Refrigerant charge, lb | 400 | 0 | 0 | 0 | 0 | 0
Refrigerant charge, lb/ton (Rc) | 0.4 | 0 | 0 | 0 | 0 | 0
Global warming potential of refrigerant (GWPr) | 77 | 77 | 1810 | 4000 | 1770 | 2080
Ozone depletion potential of refrigerant (ODPr) | 0.02 | 0.02 | 0.04 | 0 | 0 | 0
LCGWP + 100,000 × LCODP | 19.9392 | 0 | 0 | 0 | 0 | 0
Total capacity, tons | 1000
Result: | 19.9392
REMARKS
Note on A9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on B9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on C9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on D9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on E9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on F9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on G9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on A8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on B8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on C8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on D8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on E8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on F8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on G8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on A12: In 2006 leak rate data for Trane R-123 centrifugal chillers was submitted to the USGBC. A 0.5% annual leakage rate is approved for these chillers per a CIR published at www.usgbc.org
Orange = Fixed values
Turquoise = User entries
Yellow = Calculated values
Red = Ineligible result
Green = Eligible result

## Lists
Equipment type | Life
Absorption chiller | 23
Centrifugal chiller | 25
Packaged AC or HP | 15
Reciprocating chiller | 20
Screw chiller | 25
Scroll chiller | 20
Split-system AC or HP | 15
Unitary AC or HP | 15
Water cooled packaged AC | 24
Window AC or HP | 10
GWPs from IPCCv4 document
Refrigerant type | GWPr | ODPr | Ann Lk % | EOL Loss %
Ammonia | 0 | 0 | 2% | 10%
Carbon dioxide | 1 | 0 | 2% | 10%
Propane | 3 | 0 | 2% | 10%
R-123 | 77 | 0.02 | 2% | 10%
R-123_Trane_CTV_Documented_Lkg_Rate | 77 | 0.02 | 0.5% | 10%
R-1233zd(E) | 5 | 0 | 2% | 10%
R-1234yf | 4 | 0 | 2% | 10%
R-1234ze(E) | 6 | 0 | 2% | 10%
R-134a | 1430 | 0 | 2% | 10%
R-22 | 1810 | 0.04 | 2% | 10%
R-245fa | 1030 | 0 | 2% | 10%
R-32 | 675 | 0 | 2% | 10%
R-404A | 3900 | 0 | 2% | 10%
R-407A | 2100 | 0 | 2% | 10%
R-407C | 1770 | 0 | 2% | 10%
R-407F | 1820 | 0 | 2% | 10%
R-410A | 2080 | 0 | 2% | 10%
R-434A | 3240 | 0 | 2% | 10%
R-507A | 4000 | 0 | 2% | 10%
Water | 0 | 0 | 2% | 10%

## Max_Charge_Calc
Equation Calculator for USGBC LEED: v4 Energy & Atmosphere Credit; BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8
Job name
Job location
Date and time of calculation | 2014-04-28 09:55
Unit tag(s) |  | All
Refrigerant type | R-32 | Qtotal
Equipment type | Window AC or HP
Capacity, tons (Qunit) | 1 | 1
Refrigerant charge, lb | 4.09
Refrigerant charge, lb/ton (Rc) | 4.09
Leak rate, % of charge per year (Lr) | 2%
Equipment life (Life) | 10
End-of-life refrigerant loss, % of charge (Mr) | 10%
Global warming potential of refrigerant (GWPr) | 675
Ozone depletion potential of refrigerant (ODPr) | 0
Life-cycle direct global warming potential (LCGWP) | 82.8225
Life-cycle ozone depletion potential (LCODP) | 0
TSAC factor | 82.8225
TSAC factor × capacity | 82.8225 | 82.8225
| Calculation | 82.8225
| Credit? | Yes
Version 4 “Equation Calculator” for LEED, BD+C EAc4; -CS EAc4; -EB O&M EAc5;
© 2009 Trane. All rights reserved
Trane, in providing this calculation tool, assumes no responsibility for the performance or desirability of any resulting system design. Design of the HVAC system is the prerogative and responsibility of the engineering professional.
LEED Energy and Atmosphere Credit Submittal
Version 4 “Equation Calculator” for LEED, BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8;
Job name
Job location
Date | 2014-04-28 09:55
If only one type of refrigerant is used, the HVAC&R systems | comply with the formula:
OR
If multiple refrigerant types are used, the HVAC&R systems | comply with the formula:
RESULT
Using the appropriate equation, the final calculation equals | 82.8225
Based on the LEED v4 for Enhanced Refrigerant Management this project | qualifies.
CALCULATIONS
Defaults used:
2% Leakage rate per year (Lr) (except as explicitly doucmented & allowed by USGBC)
10% End-of-life loss of charge (Mr)
Equipment life varies by equipment type
ODP and GWP from LEED v4 BD+C Reference Guide
Entered values:
R-32
Unit tag(s)
Capacity, tons (Qunit) | 1
Refrigerant charge, lb | 4.09
Refrigerant charge, lb/ton (Rc) | 4.09
Global warming potential of refrigerant (GWPr) | 675
Ozone depletion potential of refrigerant (ODPr) | 0
LCGWP + 100,000 × LCODP | 82.8225
Total capacity, tons | 1
Result: | 82.8225
REMARKS
Note on A8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on B8: Capacity is a number. Using the space bar will generate an error. Please enter 0
Note on A9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on B9: Refrigerant charge is a number. Using the space bar will generate an error. Please enter 0
Note on A11: In 2006 leak rate data for Trane R-123 centrifugal chillers was submitted to the USGBC. A 0.5% annual leakage rate is approved for these chillers per a CIR published at www.usgbc.org
Orange = Fixed values
Turquoise = User entries
Yellow = Calculated values
Red = Ineligible result
Green = Eligible result
Red = Ineligible result

## Max_Charge_Table
Equation Calculator for USGBC LEED: v4 Energy & Atmosphere Credit; BD+C-EAc6; ID+C-EAc5; EB:O-M-EAc8
Maximum Refrigerant Charge Allowed (lb/ton):- Using Calculation
Equipment Life
[5 empty] | 10 | 15 | 20 | 23 | 25
Refrigerant | Leak rate | End of life Loss | GWPr | ODPr | Room or Window AC | Split or Unitary DX | Recip or Scoll Chillers | Screw or Absorption Chiillers | Centrifugal Chillers
R-123 | 2% | 10% | 77 | 0.02 | 1.6 | 1.8 | 1.92 | 1.97 | 2
R-123_Trane_CTV_Documented_Lkg_Rate | 0.5% | 10% | 77 | 0.02 | 3.2 | 4.12 | 4.81 | 5.15 | 5.34
R-1233zd(E) | 2% | 10% | 5 | 0 | 666.66 | 750 | 800 | 821.42 | 833.33
R-1234yf | 2% | 10% | 4 | 0 | 833.33 | 937.5 | 1000 | 1026.78 | 1041.66
R-1234ze(E) | 2% | 10% | 6 | 0 | 555.55 | 625 | 666.66 | 684.52 | 694.44
R-134a | 2% | 10% | 1430 | 0 | 2.33 | 2.62 | 2.79 | 2.87 | 2.91
R-22 | 2% | 10% | 1810 | 0.04 | 0.57 | 0.64 | 0.68 | 0.7 | 0.71
R-245fa | 2% | 10% | 1030 | 0 | 3.23 | 3.64 | 3.88 | 3.98 | 4.04
R-32 | 2% | 10% | 675 | 0 | 4.93 | 5.55 | 5.92 | 6.08 | 6.17
R-404A | 2% | 10% | 3900 | 0 | 0.85 | 0.96 | 1.02 | 1.05 | 1.06
R-407A | 2% | 10% | 2100 | 0 | 1.58 | 1.78 | 1.9 | 1.95 | 1.98
R-407C | 2% | 10% | 1770 | 0 | 1.88 | 2.11 | 2.25 | 2.32 | 2.35
R-407F | 2% | 10% | 1820 | 0 | 1.83 | 2.06 | 2.19 | 2.25 | 2.28
R-410A | 2% | 10% | 2080 | 0 | 1.6 | 1.8 | 1.92 | 1.97 | 2
R-434A | 2% | 10% | 3240 | 0 | 1.02 | 1.15 | 1.23 | 1.26 | 1.28
R-507A | 2% | 10% | 4000 | 0 | 0.83 | 0.93 | 1 | 1.02 | 1.04